WM-1KW WIND TURBINE

Operation Manual

**Please read carefully before using it. **

1. Application

The wind power generator is an equipment to convert wind energy into electric power which is changed into storage battery group. It can be widely used in rich wind areas but without normal energy supply from any power system .It is capable of providing power for lighting, TV, telecommunication equipment and so on.

2. Structure and Main performance

The unit is mainly composed of wind rotor, permanent magnet generator, tail vane, stand, electric controller, storage batteries, electric inverter, electric cable, etc. (Fig1)

Main technical performances

Rotor Diameter (m)	2.8

Material and number of the blades	Reinforced fibber glass*3

Rated power	1000

Rated wind speed (m/s)	9

Startup wind speed (m/s)	3

Working wind speed (m/s)	3-25

Survived wind speed	40

Rated rotate speed(r/min)	500

Working voltage	DC 48V

Generator style	Three phase, permanent magnet

Charging method	Constant voltage current saving

Speed regulation method	Tail turning and electric magnet

Stop method	Brake by hand drag

Tower height (m)	6

Weight (kg)(not including batteries	175

and inverter power supplier )

Life time	20 years

3. Preparation

3.1 Filling in electrolyte and do initial charge according to technical regulations.

3.2 Unpack and check the machine parts.

3.3 Choose an open and flat place with no barriers around for wind turbine installation.

To avoid circuit power loses, should make the distance between wind turbine and batteries as short as possible, usually it should be less than 30m.

3.4 Foundation installation

3.41 Dig a cubic hole in the center of the ground with size of 40X40X40cm. Then dig four 
	triangular pits at the place of A, B, C, and D, which are symmetrically 4 meters from the 
	central hole in four directions. The diagonals of A-C and B-D vertically intersect at the 
	center of square hole. The depth and side length are 70cm. (Fig 2)

3.42 Fix the 4 foundation bolts onto the base plate. Screw on the M16 nuts respectively until the 
	top of bolt is 15mm out of nut. Let the axe of pin dead against BD or AC. The Base plate 
	should be 4-5cm above the ground. Then adjust the base plate in level and concrete the 
	cubic hole. The mixture ratio of concrete is cement: sand: cobble= 1:2:3.

3.43 Hold the top of chain, and put the anchor horizontally into the base of pit following the 
	outboard side. Lay crushed stone (about 2~5kg) into the pits, then concrete them; Lay 
	crushed stone into the pits and concretes them again. Repeat until cram the triangular pit. 
	Finally draw the guy wires toward the ground center with an angle of 60-degree from the 
	ground. Hold the chain，concrete the pit until the middle part of the top link, the other half is 
	out of the concrete. (Fig 3)

3.44 The protection period of the concrete basement is 100 hours. During this period, don’t 
	install the wind turbines.

4. Installation procedure

4.1 Select a sunshine day without wind (wind speed smaller than 3m/s)

4.2 Adjust the Base plate in level, then put the washer onto the foundation bolt, fasten the nuts. 
	Fit together the upper, middle, lower mast. Fall the mast on the “A” pit. Link the mast bottom 
	to the base plate with Φ16 pin, then put on the washer and connects them with ringent pin.

4.3 Draw the guy wires in four directions. Bend the tip of the steel wire to a ferrule, the length of 
	which is about 20cm. Then fasten it with two wire-clamps. Put the rings for guy wires onto 
	the top of mast. Then close upon the four ferrules and thrill through the annulus of the ring 
	respectively. Finally shove them to the outshoot of mast.

4.4 Put the heart ringer for steel wire across the “o” loop of turnbuckle, and then rip the steel 
wire into the heart ringer. Bend for a ferrule; no less than 30cm long, fasten with wire-clamps. 
Hook the turnbuckles of A, B and D pits to the chain of anchor. Draw back the mast, and 
then hook the turnbuckle and anchor chain. Adjust the length of steel wire through 
turnbuckles to plumb the mast. Install the stay bar to the lower mast，fix up it with M12 bolts. 
Untie “U” shape screw between anchor and turnbuckle of pit C. Connect the steel wire of C

pit and the top of stay bar and fasten it. Then adjust until the steel wire between stay bar and mast in strain state.

4.5 Put a 1m bracket into pit A.   Loose the “U” shape screw buckle in pit B and pit D (About 
	5cm length). Untie the link of the “U” shape screw and the ground anchor chain in pit C. 
	Fall down the mast slowly; support the steel wire pothook with20cm height stow-wood.

4.6 Insert the cable through the bottom to the top of the mast with a steel wire(￠2~3mm) and 
	extend out about 20 to 50cm. Connect the 3 thrum of the cable (which derivative from the 
	slip ring) with the terminal block.

Connect the 3 thrum of the cable which derivative from the slip ring with the terminal block.

4.7 Install the generator onto the mast top through the sleeve. Fasten the screw.

4.8 Assemble the tail rod to the rotating body, setting the M10 holes correctly, insert the spring washer; screw the four M10X25 inner six angle nuts tightly. (FIG5)

4.9 There are two holes can be chosen on the trough shape clamp of the tail rod and two holes 
	distributing on the two sides of the tail vane tie-in’s axes, whose diameter is 11. Insert the 
	tie-in of tail vane into the trough shape clamp of the tail rod, insert M10X60 bolt into the ø11 
	holes correctly, put on washer10, spring washer 10 and M10 self-locked nuts, Adjust the 
	tail rod angle against the level plane according to the local wind resources and electricity 
	consumptions (it can be adjusted to four angles). Decrease the angle can increase the 
	rotating speed of the rotor. Then insert the screw shaft into ø11, screw the adjusting bolt 
	and nut (M10).   After adjusting, tighten the two self-locked nuts. (See fig.6).

4.10 Before leaving the factory, every rotor had been assembled and passed the balance 
	adjustment. For easy transport, the rotor had been disassembled. When reassembling the 
	rotor, please check the marks on the parts, so as to make them return to the former 
	positions, then fit the M10×80 screws, washers, M10 self-locked nuts one by one. Tighten 
	the nuts with a small force first, then measuring the distances between the centre point to 
	the tip end of blades a, b, c, the distance among the three sizes should less than 5mm, 
	then tighten the nuts firmly. The tighten torque should be 40 - 45 N.m (see fig.7).

4.11 Assemble the blade-rotor on the axes of generator, put on the flat washer, spring washer 
	one by one, and then screw the self-locked nut tightly。

4.12 Assemble the nose cone to the rotor hub with M6 screws, spring washers and flat 
	washers.

4.13 Draw backs the mast through chain jack; connect the screw buckle of pit C to the anchor. 
	Adjust the length of the screw buckle in four directions. Strain the steel wires to make the 
	mast in its vertical position. Strain the steel wire until it can rebound lightly when gives a 
	transverse force.

4.14 Check the wire block, screw buckle and all connecting point. Make sure it is safety. Then 
	wrap and blocked them with galvanized wire. Put anticorrosive grease on wire block, 
	screw buckle and all links where necessary.

4.15 The two connectors of battery is anode and cathode, connect them in series to be a group. 
	Choose the lead whose sectional area is 6 square millimeters as connect wire. The wire of 
	anode is marked by red color; and cathode is marked by black (or yellow, or blue). All 
	connect point should fix up by splicing fitting to ensure electric conduction is good. In 
	order to prevent acid corruptness of the splicing fitting and connecting pole, spread a layer 
	of protection grease on them..

4.16 Connect the red wire of anode of the batteries to the anode pole of the controller or 
	control-Inverter; then, connect the black wire of cathode of the batteries to the cathode 
	pole the controller or control-Inverter. Connectors must be tightened firmly and ensure 
	good electric conduction.

4.17 Connect the 3 output wires of the generator to the 3-connector poles of the controller or 
	control-inverter respectively. During the process of connecting, the “open & close” switch 
	on the controller or control-inverter box should keep on “close” position..

4.18 According to different requirements, there are two kinds of output: DC and AC. Please 
	connect according to marks on the socket. Take care for safe operation when the output is 
	AC220V.

5. Application notice

5.1 Application principles

5.1.1 Please read the specification carefully before using. Do not install or uninstall in windy 
	day.

5.1.2 The off-grid wind turbine charges the batteries through controller or control-inverter. When 
	there is no wind, it consumes the electricity from the battery group. Therefore, after 
	discharging, the batteries should be recharged timely, especially for lead-acid batteries. If 
	the batteries cannot be recharged timely after over discharging, the working life of the 
	batteries will be reduced. So, the users should regulate the consuming of electricity 
	according to local wind condition and the output of the wind generator.

5.1.3 After passing full wave bridge rectification, the 3-phase AC electricity generated by wind 
	generator output DC voltage, and then charge the battery. The voltage of the battery 
	group should be equal to the DC voltage of the wind generator (after rectification), so the 
	enginery can exert its full efficiency. The input DC voltage of matched inverter should be 
	equal to the working voltage of wind turbine.

5.1.4 The input DC voltage of the matched inverter should be equal with working voltage of the 
	wind generator (after rectification).

5.2 Safety regulations

5.2.1 Forbidden the wind generator running without any load, or running at a very high rotating 
	speed continually.

5.2.2 Checking the tower condition regularly, if there are any loosen phenomenon, it should be 
	tighten immediately, so as to prevent the falling down of the wind turbine.

5.2.3 When running speed of the rotor is higher, people are forbidden to stay under the wind 
	turbine.

5.2.4 When wind speed is more than 24 m/s, the wind turbine should be stopped artificially.

5.2.5 When vibration or strange noise is found during working, please stop the wind turbine and 
	check the reasons.

5.2.6 The power supply line of the wind generator should be arranged independently, it can not 
	be mixed used with other power supply lines. DC power supply is more safe and 
	economic for illuminators; for home electric appliances, the AC power supply line (from 
	inverter) should be used; it is suggested that the connector of the refrigerator should insert 
	in the special plug seat with time lapse function

5.2.7. When connect the electric line of the wind generating system, the battery lines must be 
	first connected to the controller & inverter box, then connect the three lines of the 
	generator to the controller. When disconnect the electric line of the wind generating 
	system, the three generator lines must be first disconnected from the controller, then 
	disconnect the two lines of the battery group from the controller & inverter box.

5.2.8 The “open & close” switch on the controller & inverter box should keep at “open” position 
	in normal conditions. Only when the batteries have been full charged or for protect the 
	system against storm wind, the switch can be put on “close” position. It is not allowed to 
	move the switch when wind is stronger and rotor is rotating at high speed, turning the 
	switch to “close” position when rotor is rotating slowly.

5.2.9. The batteries should be set on a place where far from fare resource and heat resource, 
	the gas generated from charging and discharging process should be easy go out of the 
	room.

5.3.Keep the rotor balance, eliminate vibration

When the blades lost balance caused by outside damage and create strong vibration, the 
wind generator must be stopped and checked, until the trouble is eliminated. The attached 
special tools should be used for disassembling the rotor, remove the nut and washer from 
the axes end of generator first, screw the special sleeve onto the hub firmly, then drive the 
M16×30  screw  into  the  sleeve,  so  as  to  remove  the  rotor  from  the  shaft  of  the 
generator(see fig.8). After repairing, the un-balance torque should less than 0.02N.m.

6. The maintenance of the wind generator

The products are divided into two kinds: common product and high quality product (no maintenance), the common product need following maintenances regularly.

6.1. Checking, cleaning and lubricating all rotating parts one time per year.

6.2 Before rain season, cleaning outside and paint antirust grease on the surface of all fixed connecting parts once a year.

6.3 Lubricating and maintenance bearing of generator one time per operating year.

6.4. Cleaning, rust removing and painting all exposed parts one time per every two years. The maintenance of high quality product (AA)

a. Exposed parts are made by stainless steel or have passed special long time effective rust-protection treatment, so the outside of those parts don’t need maintenance.

b. The generator has adopted high grade bearings and high grade lithium grease, the bearings 
need to be checked after operating for 5 years, if it is necessary, add some grease to the 
bearings.

7. Elimination of breakdown

The wind generator is designed and manufactured according to trouble- free and non-
maintenance principle, if the installation and operation are correct, the breakdown will not 
appear in normal conditions. In case of breakdown has happened, please consult following 
table.

Breakdown	reason	Eliminating method

Wind	generator	1. Pull rope of steel wire is loose.

vibrating strongly	2. Fixed bolts of blades are loose.

3.  Blade  is  defective  caused  by

outside force.

4. Ices over on the surface of blades,

cause unbalance.

1.  Tighten the steel wire rope appropriate.

2.  Tighten the loose parts.

3.  Replace a new one and adjust the rotor 
	to balance state again.

4. Eliminating the attached ices.

Direction regulating	1.  There is too much greasy filth in

is ineffective	the rotating body.

Rotating  part  is  deformed  by

outside force.

2.  The  clearance  between  vertical

shaft and sleeve is too small, or

there   is   no   movable   axial

clearance.

1.  Clearing away the dirty filth, and make a

lubricating maintenance.

2.  Recover and correct the deformation.

unusual noise	1.  Fixed parts is loose

2.  Generator bearing is damaged

3.  Wind rotor is rubbing with other

part.

1.  Put the wind turbine down to the ground,

check  every  fixed  part,  and  take measures.

2.  Replace the damaged bearing.

3.  Checking and eliminating the trouble.

The rotating speed	1.  Blade pitch control is ineffective.

of the wind rotor is	2.  Stator winding is short -circuit or

reduced obviously	output circuit is short pass.

3.  Break disk is rubbing.

4.  Switch is set at “close” position:

1.  Checking and eliminating the trouble,

then	making	lubrication	and

maintenance.

2.  Find out short circuit position, split the 
	lines and isolate them..

3.  Readjust the break gap.

4. Set switch at “open” position.

The output voltage	1.  The   rotating   speed   of   the

of the generator is	generator is low.

low	2.  Permanent magnet rotor has lost

its magnet.

3.  The conductivity	of connect

point between slip ring and output

circuit is weak.

4.  There is short circuit in rectifier.

5.  Circuit   line   of   low   voltage

electricity transmit is too long, or

the diameter of wire is too thin.

1.  Finding  out  the  reason,  restoring  to

normal rotating speed.

2.  Charging magnet, or change the rotor of 
	generator.

3.  Cleaning slip ring and contact point, so 
	as to reduce resistance.

4.  Replace.

5.  Shortening the circuit line or increase 
	the  diameter  of  the  wires,  so  as  to 
	reduce circuit electricity loss.

There    are    not	1. There are circuit break in AC lines

output	electric	of the generator, or the fuse is fused.

current in AC circuit	2. There are circuit break in     output

of the Generator	line.

3. Stator winding is burnt, circuit is

broken.

1.  Find out the reason, and connect the

wires.

2.  Find out the break point, then connect 
	the wires.

3.  Disassemble, then repair and recover it

AC  output  is  in	1. DC fuse is fused.	1.  Replace.

normal   condition,	2. Output circuit is broken.	2. Find out the break point and connect the

but there is not DC	wires.

output current

Output  capacity  of	1.  Output voltage of the generator is

the  batteries	is	too low, or electricity is generated

insufficient	at all.

2.	The connector of the battery is

corroded by acid, conductivity is

weak.

3.  Battery is failure

1.	Checking   and   eliminating   the

trouble.

2.	Cleaning  the  connectors,  enable

them  have  a  good  contact  and

tighten the connectors.

3.	Replace the damaged battery

WM-1KW WIND TURBINE SYSTEM

WM-1KW WIND TURBINE WIRING DRAWING